Diagnosis and Alert System - Implementation Walkthrough

Summary

Successfully implemented a comprehensive diagnosis and alert system that monitors PV system health in real-time, detects anomalies, and generates alerts. The system includes auto-resolve functionality, sensor vs inverter data comparison, and alert history tracking.

What Was Implemented

Backend Components

1. Diagnosis Engine (

diagnosis.py)

Created a comprehensive health monitoring engine with the following checks:

Voltage Monitoring:

- PV voltage range validation (150-450V default)

- Battery voltage monitoring (42-58V for 48V systems)

- AC voltage standards compliance

Current Monitoring:

- PV current limits

- Battery current thresholds

- Anomaly detection for sudden spikes

Power Discrepancy Detection:

- Compares sensor-measured power vs inverter-reported power

- Alerts when difference exceeds 15% (configurable)

- Helps identify sensor calibration issues or inverter problems

Temperature Monitoring:

- Panel temperature limits (max 85°C)

- Ambient temperature extremes

Communication Health:

- RSSI signal strength monitoring

- Weak signal warnings

2. Database Schema

Added two new tables:

alerts table:

- id (PRIMARY KEY)

- timestamp

- severity (INFO, WARNING, ERROR, CRITICAL)

- category (voltage, current, power, temperature, communication, discrepancy)

- title

- message

- component

- value

- threshold

- acknowledged (BOOLEAN)

- acknowledged_at

- resolved (BOOLEAN)

- resolved_at

diagnosis_settings table:

- id (PRIMARY KEY, always 1)

- enabled (BOOLEAN)

- thresholds (JSON)

3. API Endpoints

Alert Management:

- GET /api/alerts - Retrieve alerts with optional filtering

- GET /api/alerts/unread - Get unread alert count

- POST /api/alerts/{id}/acknowledge - Acknowledge an alert

- DELETE /api/alerts/{id} - Delete an alert

Diagnosis Settings:

- GET /api/diagnosis/settings - Get current settings

- POST /api/diagnosis/settings - Update settings

4. Auto-Resolve Feature

The system automatically resolves alerts when the issue is fixed:

- Tracks active alerts by signature

- When a condition no longer triggers an alert, it's marked as resolved

- Resolved alerts remain in history for audit purposes

Frontend Components

1. Settings Page - Diagnosis Toggle

Added a new card in Settings page:

Features:

- Checkbox to enable/disable diagnosis system

- Visual indicator (✅ Enabled / ⭕ Disabled)

- Description of what diagnosis monitors

- Real-time API communication

Location:

SettingsPage

2. Alerts Page - Real-Time Alert Display

Completely rewrote the Alerts page to show real alerts:

Features:

- Fetches alerts from backend API

- Auto-refreshes every 30 seconds

- Severity-based filtering (All, Critical, Error, Warning, Info)

- Color-coded alerts with severity icons

- Shows alert details (component, value, threshold)

- Acknowledge button for unread alerts

- Delete button for alert management

- Resolved/Acknowledged status indicators

- Relative timestamps ("2 hours ago")

Location:

AlertsPage

3. Header Alert Badge

Added a notification badge to the header:

Features:

- Shows unread alert count

- Red badge with count (9+ for >9 alerts)

- Auto-refreshes every 10 seconds

- Only visible when there are unread alerts

- Tooltip showing count

Location:

AlertBadge

How It Works

Data Flow

Measurement Data

↓

Diagnosis Engine (if enabled)

↓

Health Checks:

- Voltage ranges

- Current limits

- Power discrepancy

- Temperature

- Communication

↓

Alert Generation

↓

Database Storage

↓

Frontend Display

Auto-Resolve Logic

- Each measurement triggers diagnosis

- New alerts are saved to database

- System tracks active alert signatures

- If a previously active alert is no longer triggered, it's auto-resolved

- Resolved alerts remain in history

Example Alert Scenarios

High Voltage Alert:

Severity: WARNING

Title: High PV Voltage

Message: PV voltage from VD1 (465.2V) exceeds maximum (450V)

Component: VD1

Value: 465.2

Threshold: 450

Power Discrepancy Alert:

Severity: WARNING

Title: PV Power Mismatch

Message: Sensor PV power (3200W) differs from inverter (2100W) by 34%

Component: solar

Value: 34

Threshold: 15

Communication Issue:

Severity: WARNING

Title: Weak Signal Strength

Message: Measurement board VD1 has weak signal (RSSI: 25)

Component: VD1

Value: 25

Threshold: 30

How to Use

1. Enable Diagnosis

- Navigate to Settings page

- Find the "Diagnosis & Alerts" card

- Check the checkbox to enable

- System will start monitoring immediately

2. View Alerts

- Navigate to Alerts page

- Use filter buttons to view specific severity levels

- Click "Acknowledge" to mark alerts as read

- Click "Delete" to remove alerts from history

3. Monitor Unread Alerts

- Check the header for the red notification badge

- Number indicates unread alerts

- Badge disappears when all alerts are acknowledged/resolved

Testing the System

Test 1: Enable Diagnosis

# Backend should already be running

# Frontend should already be running

# 1. Go to Settings page

# 2. Enable diagnosis

# 3. Check backend logs for: "Diagnosis system enabled"

Test 2: Trigger High Voltage Alert

Simulate high voltage data:

# This will trigger a high voltage alert (500V exceeds 450V threshold)

curl -X POST http://localhost:8000/api/simulate \

-H "Content-Type: application/json" \

-d "{\"line\": \"500.0,5.0,98.0,5.0,48.0,10.0,230.0,8.0,1840.0,85,50\"}"

Expected Result:

- Alert appears on Alerts page

- Header badge shows "1"

- Alert details show voltage value and threshold

Test 3: Trigger Power Discrepancy

Simulate mismatch between sensor and inverter:

# Sensor shows high power, inverter shows low power

curl -X POST http://localhost:8000/api/simulate \

-H "Content-Type: application/json" \

-d "{\"line\": \"250.0,13.0,98.0,5.0,48.0,10.0,230.0,8.0,500.0,85,50\"}"

Expected Result:

- Power discrepancy alert generated

- Shows percentage difference

- Categorized as "discrepancy"

Test 4: Auto-Resolve

# 1. Trigger an alert (high voltage)

# 2. Wait 10 seconds

# 3. Send normal voltage data

curl -X POST http://localhost:8000/api/simulate \

-H "Content-Type: application/json" \

-d "{\"line\": \"250.0,5.0,98.0,5.0,48.0,10.0,230.0,8.0,1840.0,85,50\"}"

Expected Result:

- Previous high voltage alert marked as "Resolved"

- Alert becomes semi-transparent

- Shows "✓ Resolved" badge

Test 5: Acknowledge Alert

- Go to Alerts page

- Find an unread alert

- Click "Acknowledge" button

- Alert shows "👁️ Acknowledged" badge

- Header badge count decreases

Configuration

Default Thresholds

Located in

diagnosis.py:

{

'voltage': {

'pv_min': 150,

'pv_max': 450,

'battery_min': 42,

'battery_max': 58,

'ac_min': 198,

'ac_max': 264

},

'current': {

'max_pv_current': 30,

'max_battery_current': 100,

'max_ac_current': 50

},

'power_discrepancy': {

'max_percentage': 15

},

'temperature': {

'panel_max': 85,

'ambient_max': 50,

'ambient_min': -10

},

'communication': {

'min_rssi': 30

}

}

Customizing Thresholds

Thresholds can be updated via the API:

curl -X POST http://localhost:8000/api/diagnosis/settings \

-H "Content-Type: application/json" \

-d '{

"enabled": true,

"thresholds": {

"voltage": {

"pv_max": 500

}

}

}'

Files Modified/Created

Backend

- ✅

diagnosis.py - NEW

- ✅

server.py - MODIFIED

Frontend

- ✅

Pages.js - MODIFIED

- ✅

App.js - MODIFIED

Database

- ✅

pv_history.db - Auto-updated with new tables

Benefits

✅ Proactive Monitoring - Catch issues before they become problems
✅ Data Validation - Compare sensor vs inverter readings
✅ Auto-Resolve - Alerts clear automatically when fixed
✅ Alert History - Track all issues over time
✅ Configurable - Adjust thresholds to your system
✅ Real-Time - Instant notifications of issues
✅ User Control - Enable/disable as needed

Next Steps (Future Enhancements)

- Email/SMS notifications

- Configurable threshold UI

- Alert trends and analytics

- Performance degradation detection

- Predictive maintenance alerts